## scan, ocr
Fault display | Reason for fault code being triggered by control unit: | Possible cause of fault / remedy
LOW PRESSURE | The low pressure sensor has responded | Refrigerant leak, expansion valve will not open
ERR LOW PRESS | 5 LOW PRESSURE faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
MEAN PRESSURE | The limiter for minimum suction gas pressure of the high pressure compressor has responded | Refrigerant leak, expansion valve will not open, HP compressor shut-off valve will not open, non-return valve of the LP compressor bypass will not open
ERR MEAN PRESS | 5 MEAN PRESSURE faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
HIGH PRESSURE | The high pressure switch of the low pressure compressor or the high pressure switch of the high pressure compressor has responded. | Check the flow rate and sensor connection on the heating side
ERR HIGH PRESS | 5 HIGH PRESSURE faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
NO OUTPUT | High pressure < low pressure + 3 bar within 30 seconds after compressor start | Check the fuses.
ERR CMP OUTPUT | 5 NO OUTPUT faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
MIN SUPERHTG | Superheating is < minimum value for superheating within 20 minutes, applies to both superheating of the refrigerant at the evaporator output and superheating of the refrigerant at the suction gas connection of the high pressure compressor | Incorrect expansion valve function.
ERR M SUP IWS | 5 MIN SUPERHTG faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
REFRGRNT LOW | Superheating > set superheating and opening level expansion valve > limit | Refrigerant leak, incorrect expansion valve function.
ERR REF LO IWS | 5 REFRGRNT LOW faults occurred in 5 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
SPEED DEV C LP | Speed deviation between the set and actual compressor speeds greater than 5 Hz for longer than 2 minutes | Inverter or compressor not working correctly.
I INV COMP LP | Limiter for power interruption to inverter of low pressure compressor has responded | Value is reset automatically.
SUPHT INV C LP | Temperature limiter for inverter of low pressure compressor has responded | Value is reset automatically.
ROT STUCK C LP | Limiter for rotor binds for low pressure compressor has responded | Value is reset automatically.
START ERR C LP | Limiter for start error for low pressure compressor has responded | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
I INV COMP HP | Limiter for power interruption to inverter of high pressure compressor has responded | Value is reset automatically.
SUPHT INV C HP | Temperature limiter for inverter of high pressure compressor has responded | Value is reset automatically.
ROT STUCK C HP | Limiter for rotor binds for high pressure compressor has responded | Value is reset automatically.
START ERR C HP | Limiter for start error for high pressure compressor has responded | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
OUTL INV CP HP | Limiter for high pressure compressor outlet has responded | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
OUTL INV LP | Limiter for low pressure compressor outlet has responded. | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
SPEED DEV C HP | Speed deviation between the set and actual compressor speeds greater than 5 Hz for longer than 2 minutes | Inverter or compressor not working correctly.
DEFROST | Flow temperature < 10 C and low pressure < 5.2 bar during defrost | Water flow rate too low, water temperature too low.
ERR DEFROST | 5 DEFROST faults occurred in 2 hours of compressor runtime | Remove the cause. Then carry out a WPM reset.
ROTARY SWITCH | The HP type DIP switch of the IWS is set incorrectly. | Isolate the heat pump from the power supply and set the DIP switch correctly.
HP SENSOR MAX | The high pressure sensor of the low pressure compressor or the high pressure sensor of the high ressure compressor has res onded | Heating flow rate too low; selected room temperature / heatin curve too high
MAX HOT GAS T | Hot gas temperature > 130 oc | Injection valve function incorrect, expansion valve function incorrect, refrigerant leak
ERR T FLOW IWS | Sensor value of the flow sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T RTRN | Sensor value of the return sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T FROS IWS | Sensor value of the frost protection sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T COND IWS | Sensor value of the condenser outlet sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
NO IWS PARAM | Heat pump type was not transferred to the controller | Select heat pump via heat pump type parameter
ERR OTS IWS | Sensor value of the outside temperature sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T EXP lws | Sensor value of the exhaust air sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR SUC TC HP | Sensor value of the suction gas temperature sensor for high pressure compressor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR SUC T C LP | Sensor value of the suction gas temperature sensor for low pressure compressor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T EVAP IWS | Sensor value of the evaporator temperature sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR T HTG IWS | Sensor value of the hot gas temperature sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR OIL SUMP | Sensor value of the oil sump temperature sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR LP SENSOR | Sensor value of the low pressure sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR MP SENSOR | Sensor value of the mean pressure sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR HP SENSOR | Sensor value of the high pressure sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR EV DIFF PR | Sensor value of the differential pressure sensor outside the permissible range | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
ERR POWER | Value of the current sensor outside the permissible range | Check leads and the relevant plug-in connectors, and replace if faulty
ERR OIL BAL | Oil compensation valve will not open/close | Check leads and the relevant plug-in connectors, and replace if faulty
COM IN IWS CSW | Limiter communication interruption IWS/CWS | Check leads and the relevant plug-in connectors, and replace if faulty
INVN DSP COM | INV minor fault DSP interrupted after comm | Inverter fault
INVN COM DSP | INV minor fault comm interrupted after DSP | Inverter fault
INVN SCR TMIN | INV minor fault scroll low temperature | Inverter fault
INVN MOT TMIN | INV minor fault scroll low temperature | Inverter fault
INVN BRD TMIN | INV minor fault circuit low temperature | Inverter fault
INVN INV TMIN | INV minor fault inverter low temperature | Inverter fault
INVN PFC TMIN | INV minor fault PFC low temperature | Inverter fault
INVN FATAL ERR | INV minor fault, fault limit lockout | Inverter fault
SOA LP MIN | Low pressure below SOA LP limit for impermissible length of time | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
SOA LP MAX | Low pressure above SOA LP limit for impermissible length of time | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
SOA LP AREA | SOA range exceeded | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
SOA HP MIN | High pressure below SOA HP limit for impermissible length of time | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
SOA HP MAX | High pressure above SOA HP limit for impermissible length of time | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
SOA HP AREA | SOA range exceeded | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
INVH INV IMAX | INV major fault inverter excess current | Inverter fault
INVH PFC IMAX | INV major fault PFC excess current | Inverter fault
INVH DC UMAX | INV major fault DC excess voltage | Inverter fault
INVH DC UMIN | INV major fault DC undervoltage | Inverter fault
INVH AC UMAX | INV major fault AC excess voltage | Inverter fault
INVH AC UMIN | INV major fault AC undervoltage | Inverter fault
INVH AC UBAI | INV major fault AC voltage balance | Inverter fault
INVH ENTSAETT | INV major fault desaturation | Inverter fault
INVH INV TMAX | INV major fault inverter excess temperature | Inverter fault
INVH PFC TMAX | INV major fault PFC excess tem erature | Inverter fault
INVH AUST | INV major fault rotor vector | Inverter fault
INVH ARITHMET | INV major fault arithmetic | Inverter fault
INVH REL OFFEN | INV major fault input relay open | Inverter fault
INVH INV IBAL | INV major fault inverter current balance | Inverter fault
INVH PFC IBAL | INV major fault PFC current balance | Inverter fault
INVH SELV BER | INV major fault low voltage range exceeded | Inverter fault
INVH MOT NMAX | INV major fault motor excess s eed | Inverter fault
INVN DC UMIN | INV minor fault DC undervoltage | Inverter fault
INVN MOM MAX | INV minor fault torque limit | Inverter fault
INVN MODBUS | INV minor fault Modbus error | Inverter fault
INVN SCR TMAX | INV minor fault scroll excess temperature | Inverter fault
INVN MOT TMAX | INV minor fault motor excess temperature | Inverter fault
INVN BRD TMAX | INV minor fault circuit excess temperature | Inverter fault
INVN INV TMAX | INV minor fault inverter excess temperature | Inverter fault
INVN PFC TMAX | INV minor fault PFC excess temperature | Inverter fault
INVN INV TBAL | INV minor fault inverter temperature balance | Inverter fault
INVN PFC TBAL | INV minor fault PFC temperature balance | Inverter fault
INVN ADC COM | INV minor fault ADC communication error | Inverter fault
KOMM U IWS IN | Limiter low priority communication interruption IWS/INV | Inverter fault. Check wiring and associated plug-in connectors; replace if faulty. Check inverter power supply.
KOMM U IWS I H | Limiter high priority communication interruption IWS/INV | Inverter fault. Check wiring and associated plug-in connectors; replace if faulty. Check inverter power supply.
INVH SAMMELI G | INV major fault central fault 1 unresolved | Inverter fault
INVH SAMMEL1 | INV major fault central fault 1 | Inverter fault
INVH SAMMEL2 G | INV major fault central fault 2 unresolved | Inverter fault
INVH SAMMEL2 | INV major fault central fault 2 | Inverter fault
INVN SAMMEL1 G | INV minor fault central fault 1 unresolved | Inverter fault
INVN SAMMEL1 | INV minor fault central fault 1 | Inverter fault
INVN SAMMEL2 G | INV minor fault central fault 2 unresolved | Inverter fault
INVN SAMMEL2 | INV minor fault central fault 2 | Inverter fault
INVN EXT ERR | INV major fault external | Inverter fault

## ok
Known Err code hex | Known Err code dec | Column1 | Err code hex | Column2 | Fault display | Column3 | Reason for fault code being triggered by control unit: | Column4 | Possible cause of fault / remedy
| 27 | (number: $ | 001B | ; display: ' | LOW PRESSURE | '; descr: ' | The low-pressure sensor has responded | '), | Refrigerant leak, expansion valve will not open
|  | (number: $ | 0000 | ; display: ' | ERR LOW PRESS | '; descr: ' | 5 LOW PRESSURE faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
| 7 | (number: $ | 0007 | ; display: ' | MEAN PRESSURE | '; descr: ' | The limiter for minimum suction gas pressure of the high-pressure compressor has responded | '), | Refrigerant leak, expansion valve will not open, HP compressor shut-off valve will not open, non-return valve of the LP compressor bypass will not open
|  | (number: $ | 0000 | ; display: ' | ERR MEAN PRESS | '; descr: ' | 5 MEAN PRESSURE faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
| 28 | (number: $ | 001C | ; display: ' | HIGH PRESSURE | '; descr: ' | The high-pressure switch of the low-pressure compressor or the high-pressure switch of the high-pressure compressor has responded. | '), | Check the flow rate and sensor connection on the heating side
|  | (number: $ | 0000 | ; display: ' | ERR HIGH PRESS | '; descr: ' | 5 HIGH PRESSURE faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
| 34 | (number: $ | 0022 | ; display: ' | NO OUTPUT | '; descr: ' | High pressure < low pressure + 3 bar within 30 seconds after compressor start | '), | Check the fuses.
|  | (number: $ | 0000 | ; display: ' | ERR CMP OUTPUT | '; descr: ' | 5 NO OUTPUT faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
|  | (number: $ | 0000 | ; display: ' | MIN SUPERHTG | '; descr: ' | Superheating is < minimum value for superheating within 20 minutes, applies to both superheating of the refrigerant at the evaporator output and superheating of the refrigerant at the suction gas connection of the high-pressure compressor | '), | Incorrect expansion valve function.
| 35 | (number: $ | 0023 | ; display: ' | ERR M SUP IWS | '; descr: ' | 5 MIN SUPERHTG faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
|  | (number: $ | 0000 | ; display: ' | REFRGRNT LOW | '; descr: ' | Superheating > set superheating and opening level expansion valve > limit | '), | Refrigerant leak, incorrect expansion valve function.
| 37 | (number: $ | 0025 | ; display: ' | ERR REF LO IWS | '; descr: ' | 5 REFRGRNT LOW faults occurred in 5 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
|  | (number: $ | 0000 | ; display: ' | SPEED DEV C LP | '; descr: ' | Speed deviation between the set and actual compressor speeds greater than 5 Hz for longer than 2 minutes | '), | Inverter or compressor not working correctly.
|  | (number: $ | 0000 | ; display: ' | I INV COMP LP | '; descr: ' | Limiter for power interruption to inverter of low-pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | SUPHT INV C LP | '; descr: ' | Temperature limiter for inverter of low-pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | ROT STUCK C LP | '; descr: ' | Limiter for rotor binds for low pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | START ERR C LP | '; descr: ' | Limiter for start error for low pressure compressor has responded | '), | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
|  | (number: $ | 0000 | ; display: ' | I INV COMP HP | '; descr: ' | Limiter for power interruption to inverter of high-pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | SUPHT INV C HP | '; descr: ' | Temperature limiter for inverter of high-pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | ROT STUCK C HP | '; descr: ' | Limiter for rotor binds for high pressure compressor has responded | '), | Value is reset automatically.
|  | (number: $ | 0000 | ; display: ' | START ERR C HP | '; descr: ' | Limiter for start error for high pressure compressor has responded | '), | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
|  | (number: $ | 0000 | ; display: ' | OUTL INV CP HP | '; descr: ' | Limiter for high pressure compressor outlet has responded | '), | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
|  | (number: $ | 0000 | ; display: ' | OUTL INV LP | '; descr: ' | Limiter for low pressure compressor outlet has responded. | '), | Mains voltage for compressor supply may be too low or mains impedance of the compressor supply may be too high
|  | (number: $ | 0000 | ; display: ' | SPEED DEV C HP | '; descr: ' | Speed deviation between the set and actual compressor speeds greater than 5 Hz for longer than 2 minutes | '), | Inverter or compressor not working correctly.
| 42 | (number: $ | 002A | ; display: ' | DEFROST | '; descr: ' | Flow temperature < 10 C and low pressure < 5.2 bar during defrost | '), | Water flow rate too low, water temperature too low.
|  | (number: $ | 0000 | ; display: ' | ERR DEFROST | '; descr: ' | 5 DEFROST faults occurred in 2 hours of compressor runtime | '), | Remove the cause. Then carry out a WPM reset.
| 8 | (number: $ | 0008 | ; display: ' | ROTARY SWITCH | '; descr: ' | The HP type DIP switch of the IWS is set incorrectly. | '), | Isolate the heat pump from the power supply and set the DIP switch correctly.
1D | 29 | (number: $ | 001D | ; display: ' | HP SENSOR MAX | '; descr: ' | The high-pressure sensor of the low-pressure compressor or the high-pressure sensor of the high-pressure compressor has responded | '), | Heating flow rate too low; selected room temperature / heating curve too high
|  | (number: $ | 0000 | ; display: ' | MAX HOT GAS T | '; descr: ' | Hot gas temperature > 130 °C | '), | Injection valve function incorrect, expansion valve function incorrect, refrigerant leak
| 40 | (number: $ | 0028 | ; display: ' | ERR T FLOW IWS | '; descr: ' | Sensor value of the flow sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 41 | (number: $ | 0029 | ; display: ' | ERR T RETURN IWS | '; descr: ' | Sensor value of the return sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | ERR T FROS IWS | '; descr: ' | Sensor value of the frost protection sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | ERR T COND IWS | '; descr: ' | Sensor value of the condenser outlet sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | NO IWS PARAM | '; descr: ' | Heat pump type was not transferred to the controller | '), | Select heat pump via heat pump type parameter
| 22 | (number: $ | 0016 | ; display: ' | ERR OTS IWS | '; descr: ' | Sensor value of the outside temperature sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | ERR T EXP IWS | '; descr: ' | Sensor value of the exhaust air sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 10 | (number: $ | 000A | ; display: ' | ERR SUC T C HP | '; descr: ' | Sensor value of the suction gas temperature sensor for high pressure compressor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 11 | (number: $ | 000B | ; display: ' | ERR SUC T C LP | '; descr: ' | Sensor value of the suction gas temperature sensor for low pressure compressor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 20 | (number: $ | 0014 | ; display: ' | ERR T EVAP IWS | '; descr: ' | Sensor value of the evaporator temperature sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 18 | (number: $ | 0012 | ; display: ' | ERR T HTG IWS | '; descr: ' | Sensor value of the hot gas temperature sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | ERR OIL SUMP | '; descr: ' | Sensor value of the oil sump temperature sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 32 | (number: $ | 0020 | ; display: ' | ERR LP SENSOR | '; descr: ' | Sensor value of the low-pressure sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 9 | (number: $ | 0009 | ; display: ' | ERR MP SENSOR | '; descr: ' | Sensor value of the mean pressure sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 31 | (number: $ | 001F | ; display: ' | ERR HP SENSOR | '; descr: ' | Sensor value of the high-pressure sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 8002 | (number: $ | 1F42 | ; display: ' | ERR EV DIFF PR | '; descr: ' | Sensor value of the differential pressure sensor outside the permissible range | '), | Check sensor, leads and the relevant plug-in connectors, and replace if faulty
| 8009 | (number: $ | 1F49 | ; display: ' | ERR POWER | '; descr: ' | Value of the current sensor outside the permissible range | '), | Check leads and the relevant plug-in connectors, and replace if faulty
| 8010 | (number: $ | 1F4A | ; display: ' | ERR OIL BAL | '; descr: ' | Oil compensation valve will not open/close | '), | Check leads and the relevant plug-in connectors, and replace if faulty
|  | (number: $ | 0000 | ; display: ' | COM IN IWS CSW | '; descr: ' | Limiter communication interruption IWS/CWS | '), | Check leads and the relevant plug-in connectors, and replace if faulty
| 8134 | (number: $ | 1FC6 | ; display: ' | INVN DSP COM | '; descr: ' | INV minor fault DSP interrupted after comm | '), | Inverter fault
| 8135 | (number: $ | 1FC7 | ; display: ' | INVN COM DSP | '; descr: ' | INV minor fault comm interrupted after DSP | '), | Inverter fault
| 8136 | (number: $ | 1FC8 | ; display: ' | INVN SCR TMIN | '; descr: ' | INV minor fault scroll low temperature | '), | Inverter fault
| 8137 | (number: $ | 1FC9 | ; display: ' | INVN MOT TMIN | '; descr: ' | INV minor fault scroll low temperature | '), | Inverter fault
| 8138 | (number: $ | 1FCA | ; display: ' | INVN BRD TMIN | '; descr: ' | INV minor fault circuit low temperature | '), | Inverter fault
| 8139 | (number: $ | 1FCB | ; display: ' | INVN INV TMIN | '; descr: ' | INV minor fault inverter low temperature | '), | Inverter fault
| 8140 | (number: $ | 1FCC | ; display: ' | INVN PFC TMIN | '; descr: ' | INV minor fault PFC low temperature | '), | Inverter fault
1FCD | 8141 | (number: $ | 1FCD | ; display: ' | INVN FATAL ERR | '; descr: ' | INV minor fault, fault limit lockout | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | SOA LP MIN | '; descr: ' | Low pressure below SOA LP limit for impermissible length of time | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
|  | (number: $ | 0000 | ; display: ' | SOA LP MAX | '; descr: ' | Low pressure above SOA LP limit for impermissible length of time | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
|  | (number: $ | 0000 | ; display: ' | SOA LP AREA | '; descr: ' | SOA range exceeded | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
|  | (number: $ | 0000 | ; display: ' | SOA HP MIN | '; descr: ' | High pressure below SOA HP limit for impermissible length of time | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
|  | (number: $ | 0000 | ; display: ' | SOA HP MAX | '; descr: ' | High pressure above SOA HP limit for impermissible length of time | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
|  | (number: $ | 0000 | ; display: ' | SOA HP AREA | '; descr: ' | SOA range exceeded | '), | Refrigerant circuit cannot adjust operating conditions to SOA range for compressor
1FAA | 8106 | (number: $ | 1FAA | ; display: ' | INVH INV IMAX | '; descr: ' | INV major fault inverter excess current | '), | Inverter fault
| 8107 | (number: $ | 1FAB | ; display: ' | INVH PFC IMAX | '; descr: ' | INV major fault PFC excess current | '), | Inverter fault
| 8108 | (number: $ | 1FAC | ; display: ' | INVH DC UMAX | '; descr: ' | INV major fault DC excess voltage | '), | Inverter fault
1FAD | 8109 | (number: $ | 1FAD | ; display: ' | INVH DC UMIN | '; descr: ' | INV major fault DC undervoltage | '), | Inverter fault
| 8110 | (number: $ | 1FAE | ; display: ' | INVH AC UMAX | '; descr: ' | INV major fault AC excess voltage | '), | Inverter fault
1FAF | 8111 | (number: $ | 1FAF | ; display: ' | INVH AC UMIN | '; descr: ' | INV major fault AC undervoltage | '), | Inverter fault
1FB0 | 8112 | (number: $ | 1FB0 | ; display: ' | INVH AC UBAL | '; descr: ' | INV major fault AC voltage balance | '), | Inverter fault
| 8113 | (number: $ | 1FB1 | ; display: ' | INVH ENTSAETT | '; descr: ' | INV major fault desaturation | '), | Inverter fault
| 8114 | (number: $ | 1FB2 | ; display: ' | INVH INV TMAX | '; descr: ' | INV major fault inverter excess temperature | '), | Inverter fault
| 8115 | (number: $ | 1FB3 | ; display: ' | INVH PFC TMAX | '; descr: ' | INV major fault PFC excess temperature | '), | Inverter fault
1FB4 | 8116 | (number: $ | 1FB4 | ; display: ' | INVH AUST | '; descr: ' | INV major fault rotor vector | '), | Inverter fault
| 8117 | (number: $ | 1FB5 | ; display: ' | INVH ARITHMET | '; descr: ' | INV major fault arithmetic | '), | Inverter fault
1FB6 | 8118 | (number: $ | 1FB6 | ; display: ' | INVH REL OFFEN | '; descr: ' | INV major fault input relay open | '), | Inverter fault
| 8119 | (number: $ | 1FB7 | ; display: ' | INVH INV IBAL | '; descr: ' | INV major fault inverter current balance | '), | Inverter fault
| 8120 | (number: $ | 1FB8 | ; display: ' | INVH PFC IBAL | '; descr: ' | INV major fault PFC current balance | '), | Inverter fault
| 8121 | (number: $ | 1FB9 | ; display: ' | INVH SELV BER | '; descr: ' | INV major fault low voltage range exceeded | '), | Inverter fault
| 8122 | (number: $ | 1FBA | ; display: ' | INVH MOT NMAX | '; descr: ' | INV major fault motor excess speed | '), | Inverter fault
1FBB | 8123 | (number: $ | 1FBB | ; display: ' | INVN DC UMIN | '; descr: ' | INV minor fault DC undervoltage | '), | Inverter fault
| 8124 | (number: $ | 1FBC | ; display: ' | INVN MOM MAX | '; descr: ' | INV minor fault torque limit | '), | Inverter fault
| 8125 | (number: $ | 1FBD | ; display: ' | INVN MODBUS | '; descr: ' | INV minor fault Modbus error | '), | Inverter fault
1FBE | 8126 | (number: $ | 1FBE | ; display: ' | INVN SCR TMAX | '; descr: ' | INV minor fault scroll excess temperature | '), | Inverter fault
| 8127 | (number: $ | 1FBF | ; display: ' | INVN MOT TMAX | '; descr: ' | INV minor fault motor excess temperature | '), | Inverter fault
| 8128 | (number: $ | 1FC0 | ; display: ' | INVN BRD TMAX | '; descr: ' | INV minor fault circuit excess temperature | '), | Inverter fault
| 8129 | (number: $ | 1FC1 | ; display: ' | INVN INV TMAX | '; descr: ' | INV minor fault inverter excess temperature | '), | Inverter fault
| 8130 | (number: $ | 1FC2 | ; display: ' | INVN PFC TMAX | '; descr: ' | INV minor fault PFC excess temperature | '), | Inverter fault
| 8131 | (number: $ | 1FC3 | ; display: ' | INVN INV TBAL | '; descr: ' | INV minor fault inverter temperature balance | '), | Inverter fault
| 8132 | (number: $ | 1FC4 | ; display: ' | INVN PFC TBAL | '; descr: ' | INV minor fault PFC temperature balance | '), | Inverter fault
| 8133 | (number: $ | 1FC5 | ; display: ' | INVN ADC COM | '; descr: ' | INV minor fault ADC communication error | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | KOMM U IWS IN | '; descr: ' | Limiter low priority communication interruption IWS/INV | '), | Inverter fault. Check wiring and associated plug-in connectors; replace if faulty. Check inverter power supply.
|  | (number: $ | 0000 | ; display: ' | KOMM U IWS I H | '; descr: ' | Limiter high priority communication interruption IWS/INV | '), | Inverter fault. Check wiring and associated plug-in connectors; replace if faulty. Check inverter power supply.
|  | (number: $ | 0000 | ; display: ' | INVH SAMMELI G | '; descr: ' | INV major fault central fault 1 unresolved | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVH SAMMEL1 | '; descr: ' | INV major fault central fault 1 | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVH SAMMEL2 G | '; descr: ' | INV major fault central fault 2 unresolved | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVH SAMMEL2 | '; descr: ' | INV major fault central fault 2 | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVN SAMMEL1 G | '; descr: ' | INV minor fault central fault 1 unresolved | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVN SAMMEL1 | '; descr: ' | INV minor fault central fault 1 | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVN SAMMEL2 G | '; descr: ' | INV minor fault central fault 2 unresolved | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVN SAMMEL2 | '; descr: ' | INV minor fault central fault 2 | '), | Inverter fault
|  | (number: $ | 0000 | ; display: ' | INVN EXT ERR | '; descr: ' | INV major fault external | '), | Inverter fault
0 | 0 | (number: $ | 0000 | ; display: ' | No error | '; descr: ' | No error | '), | No error